## Slide 1
Energy Efficiency in
Thermal processes
Gema Millán
Inmaculada Fraj
This project has received funding from the European Union’s H2020 Coordination Support Action under Grant Agreement No.785047.
Towards a Sustainable Agro-Food Industry Capacity Building Programmes in Energy Efficiency

## Slide 2: Energy Efficiency in boilers Energy Efficiency in dryers
01
02
CONTENTS

## Slide 3
Energy Efficiency in Boilers
01

## Slide 4
Different types of boilers can be classified by the following characteristics:
Type of combustion chamber
Efficiency rate
Type of fuel
atmospheric pressure
watertight or airtight
Conventional
Low temperature
Condensation
Solid fuels: biomass or coal
Liquid fuels: fueloil or diesel
Gaseous fuels: natural gas, propane, butane
Type of heat exchanger device
water pipe
gas pipe
Energy Efficiency in Boilers
01

## Slide 5
Analyzing the combustion chamber, these are the main differences between both type of boilers:
Energy Efficiency in Boilers
01
In steam boilers: - Aquotubular - Pyrotubular | atmospheric | watertight or airtight
Description | - The combustion chamber is opened. - The air, that is necessary for the combustion, is taken from the space where the boiler is installed. | - The combustion chamber is watertight and airtight. - The air is obtained by means of a concentric pipe located in the top. - These pipe are also used to expel flue gases.
Security | - These boilers are less safe. - The combustion chamber is not insulated. | - These boilers are safer
Legislation | Since 1st January 2010 the installation of these boilers is forbidden in European Countries. | 

## Slide 6
Analyzing the combustion chamber these are the main differences in boilers:
watertight and airtight
atmospheric
Energy Efficiency in Boilers
01
Notes: The atmospheric boilers take the air for the combustion from the same place where are installed, and the airtight boiler takes the air from outside, there is an extractor that forces air inlet and outlet.

## Slide 7
Analyzing the way to exchange heat, there are the following types:
The fluid to be heated flows through several pipes that surround the combustion chamber.
Exhaust gases flow through a grid of pipes that are in direct contact with the flow of water.
Energy Efficiency in Boilers
01
Gas pipe
Water pipe

## Slide 8
Analyzing the way to exchange heat, there are the following types:
Energy Efficiency in Boilers
01
Water pipe
Gas pipe

## Slide 9
Analyzing the type of efficiency
European Directive 92/42 CEE classify boilers according to the minimum temperature boilers can operate and the efficiency.
Standard (3): are commonly use to produce hot water at a constant temperature from 70ºC to 90ºC
Low temperature (2): the return water temperature is from 35ºC to 40ºC. The lower the temperature, the higher the efficiency.
Condensation (1): they are designed to condense water vapor found in the exhaust gases. It takes advantage of the heat of condensation.
Energy Efficiency in Boilers
01
Type of boiler | Fuel safe (%)
Standard | ---
Low temperature | 8-10%
Condensation | 18-20%

## Slide 10
Analyzing the type of efficiency
Energy Efficiency in Boilers
01
 | Standard | Low temperature | Condensation
Fuel type | Diesel, propane, natural gas | Diesel, propane, natural gas | Only natural gas
Characteristics | It operates at high temperatures | Input water temperature is lower than in a standard | It condensates the water from the exhaust gases
Efficiency | 80-85% | 90-95% | 100-105%
Energy savings |  | Aprox. 15% | Aprox. 25%

## Slide 11
Low temperature boilers
The return temperature is from 35ºC to 40ºC,
These boilers can adjust the operation temperature according to the demand,
With respect to the standard boilers, the savings can be reached 15 %.
Condensing boilers
Is similar to a low temperature boiler but it is prepared to condense most of the water contained in the flue gases (water also has energy and this quantity is very high in the process of condensation),
It can only run on natural gas because it has no sulfur in exhaust gas,
These are the most efficient with values higher than 100 % in case the condensation energy is used.
Energy Efficiency in Boilers
01

## Slide 12
Some concepts about condensation boilers:
What is the energy of the water?
The specific heat of water at atmospheric pressure is: 4.18 kJ/kg ºC
This means that is necessary 4.18 kJ to increase
1ºC a quantity of 1 kg of water
However, the latent heat of vaporization is defined as the amount of heat that is required to pass from the liquid phase to the vapor at a constant temperature at the point of phase change.
At this point, the water at atmospheric pressure needs 2257 kJ/kg to increase only 1ºC. In the case of changing steam to liquid, the steam gives 2257 kJ/kg, so the boilers that can use this energy are very efficient.
Energy Efficiency in Boilers
01

## Slide 13
analyzing fuels: (lower calorific value and CO2 emissions)
Natural gas = 9.545 kcal/kg
Propane = 11.082 kcal/kg
Butane = 10.938 kcal/kg
Petrol = 10.514 kcal/kg
Diesel = 10.200 kcal/kg
Querosene = 10.382 kcal/kg
Olive pomace = 4.282 kcal/kg
Grape pomace = 4.575 kcal/kg
Pellet = 4,357 kcal/kg
CO2 emissions in several fuels
Natural gas = 2,15 kgCO2/Nm3
Propane = 2,94 kgCO2/kg
Butane = 2,96 kgCO2/kg
Petrol = 2,38 kgCO2/l
Diesel = 2,79 kgCO2/l
Biomass = 0 kgCO2/kg
Energy Efficiency in Boilers
01

## Slide 14
In the combustion process, the following characteristics take part:
1.- The most used fuels are the organic materials that are formed mainly by Carbon and Hydrogen,
2.- The higher the proportion of hydrogen, the cleaner the combustion will be and the higher the calorific value of the fuel,
3.- The better the mixture between fuel and oxygen, the more efficient combustion will be.
The most important chemical reactions that take place in the combustion are the following:
C + O2  CO2 + 32,8 MJ/kg
H2 + ½ O2  H2O + 142 MJ/kg
S + O2  SO2 + 165 MJ/kg
Energy Efficiency in Boilers
01

## Slide 15
Operation flow scheme of a boiler
boiler
Exhaust gases
Fuel
air
air
Cold water
Hot water or steam
Energy Efficiency in Boilers
01

## Slide 16
In the operation of a boiler there are two independent circuits: one from water and other for gases.
Hot water
Cool water
gases output
fuel input
burner
Gas circuit
Energy Efficiency in Boilers
01

## Slide 17
Performance evaluation of a boiler
The heat that can be obtained in a combustion corresponds to the calorific value of the fuel (and also to the water content in the air in the case of condensing boilers).
When combustion takes place, part of the heat is lost through the boiler and the exhaust gases.
Energy Efficiency in Boilers
01

## Slide 18
The main losses are:
Heat losses in combustion gases
Losses because the fuel is not completely burned
Radiation losses
Heat losses due to air existence in the water circuit
Evaluation of the performance of a boiler
Energy Efficiency in Boilers
01
Performance (%) = 100 - losses

## Slide 19
Performance evaluation of a boiler
Case 1: heating boiler
By means of this procedure, it is necessary to measure the water flow rate inside the boiler, its input and output temperatures and fuel consumption.
η = performance
m = water flow (kg/s)
Cp = specific heat capacity of water (kJ/kgºC)
ΔT = T out – T in
F = fuel consumption (Nm3/s)
PCI = fuel lower heat power (kJ/Mm3)
Energy Efficiency in Boilers
01

## Slide 20
In this case the boiler produces a flow of steam, so that its pressure or temperature, the input temperature and the fuel consumption influence the performance
η = performance
Pv = steam production (kg/h)
Hv = steam enthalpy (kJ/kg)
Hfe = input enthalpy to the fluid (kJ/kg)
b = fuel flow input (kg/h or Nm3/h)
PCI = lower calorific value of fuel (kJ/Nm3)
Performance evaluation of a boiler
Case 2: steam boiler
Eficiencia energética en calderas
01

## Slide 21
The thermodynamic properties of water depends on the state.
This state can be defined from temperature and pressure.
The enthalpy depends on the thermodynamic state and therefore influences the production of heat.
Water steam at 1 bar and 99,63 ºC  steam enthalpy = 2675 kJ/kg
Water steam at 7 bar and 165 ºC  steam enthalpy = 2763,5 kJ/kg
Energy Efficiency in Boilers
01

## Slide 22
The gas analyzer measures the energy efficiency and the quality of the exhaust
heat loss in the exhaust gas
losses for fuel that has not been burned
Determine the performance of a boiler
Energy Efficiency in Boilers
01

## Slide 23
What parameters can be measured with the gases analyzer?
Oxygen (O2)
The oxygen that has not been used in the combustion is due to the fact that in the reaction there is an excess of oxygen and, therefore, it is expelled through the exhaust gases.
Oxygen measurement provides very useful information about combustion performance.
Typical values of oxygen concentration in the exhaust gases:
  Diesel boiler = 2 % - 5 %
  Natural gas boiler = 2 % - 6 %
Energy Efficiency in Boilers
01

## Slide 24
Carbon monoxide (CO)
Carbon monoxide is a toxic gas, it is also odorless and invisible and is produced as a result of incomplete combustion.
Typical values of CO concentration in the exhaust gases:
  Diesel boiler = 80 – 150 ppm
  Natural gas boiler = 80 – 100 ppm
What parameters can be measured with the gases analyzer?
Eficiencia energética en calderas
01

## Slide 25
Temperature of flue gases:
A high temperature of the exhaust gases can be as a consequence of:
Too much air velocity at the entrance, which makes the contact time of the gases with the surfaces of the heat exchanger difficult,
Dirt on the surfaces of the heat exchanger that makes heat exchange difficult,
Incorrect operation of the burner
Poor boiler design, inadequate way of expelling fumes
Typical values are: temperature of the flue gases < fluid temperature + 65ºC
What parameters can be measured with the gases analyzer?
1
2
3
4
Energy Efficiency in Boilers
01

## Slide 26
Excess of air
The amount of stoichiometric oxygen (minimum value) is not enough to make a complete combustion, because the mixture of fuel and oxygen is not perfect. Therefore, it is necessary to provide more combustion air.
This additional amount of air is known as “excess air”, the ratio of the actual amount of air to the stoichiometric amount needed is known as the excess air coefficient (λ).
The highest combustion efficiency is obtained when there is a minimum “excess air” because it is necessary to heat less air mass.
A high excess of air reduces the temperature of combustion and needs more energy from the fuels because there is more volume of gas.
However, an adequate excess of aire is necessary, because if the excess of air is too low, there will be a deficient performance in the use of fuel and there will be more unburned fuel in the exhaust gases with the associated negative environmental impact.
What parameters can be measured with the gases analyzer?
Energy Efficiency in Boilers
01

## Slide 27
Excess of air
a) The excess of air can be directly measured with the gas analyzer
b) The excess of air can be calculated following an equation
Percentage of oxygen in the fumes.
Percentage oxygen in the air.
What parameters can be measured with the gases analyzer?
Energy Efficiency in Boilers
01
λ =

## Slide 28
What parameters can be measured with the gas analyzer?
Energy Efficiency in Boilers
01
Analyze values | Cause | Solution
High CO level Low O2 level | Cause | Solution
Low CO2 level High O2 level | Insufficient air is introduced into the boiler | Increase the air flow that crosses the burner
Low CO2 level High O2 level | Excess air | Reduce airflow through the intake valve to the burner
High CO level High O2 level | Inadequate mix air – fuel | Clean the burner injector
Walls temperatures > room temperature | Old boiler with insufficient isolation | Replace insulation
Exhaust gases temperature > 230 ºC | Inadequate heat exchanger | Clean the inner of the boiler

## Slide 29
Heat losses in the combustion gases:
Losses = fumes flow (kg/Nm3comb) x (fumes enthalpy (kcal/kg fumes)
Energy Efficiency in Boilers
01

## Slide 30
Radiation losses:
These losses are very easy to detect, but it is difficult to determine how much heat is lost.
Energy Efficiency in Boilers
01

## Slide 31
Radiation losses:
Diferencia de temperatura (interior - exterior)
Pérdidas por radicación (w/m2)
Energy Efficiency in Boilers
01

## Slide 32
Measures that can be taken to improve energy efficiency in boilers:
  Regulation of combustion
  Flue gas heat recovery
  Insulation of pipes
  Condensate heat recovery
  Heat recovery from boiler purges
1
2
3
4
5
Energy Efficiency in Boilers
01

## Slide 33
Regulation of combustion:
It is the control of the air/fuel mixture, it is crucial to obtain a high performance in the boiler. It is necessary to have enough air for a total combustion, but being careful, because too much air will produce losses.
The optimum amount of excess air changes according to the operation conditions so it is necessary to have an automatic regulation.
Regulation controlling O2
Regulation controlling CO/H2
Through the lambda sensor:
In 15 sec it adjusts the air excess.
This sensor analyzes the exhaust gases and adjusts excess air through the air intake to the burner.
It affects the fuel and air mixture by controlling the CO2
Energy Efficiency in Boilers
01
1

## Slide 34
Flue gas heat recovery - economizer:
One of the most used devices to increase the performance is to preheat the incoming water by means of an “economizer”.
Its function is to use the temperature of the exhaust gases to preheat the incoming water, saving the energy needed to heat this amount of water and reduce losses.
It is not possible to reduce as much as we want the temperature of the exhaust gases because problems can occur due to corrosion in case of condensation as a consequence of the sulfur content in the fuel.
Energy Efficiency in Boilers
01
2

## Slide 35
Recovery of heat from exhaust gases - preheater:
The air flowing to carry out the combustion is preheated, so in this case the water in the boiler circuit is not heated, the air used for combustion is heated.
More heat exchange surface is needed.
Eficiencia energética en calderas
01
2

## Slide 36
Pipes isolation:
3
Energy Efficiency in Boilers
01

## Slide 37
Pipes isolation:
It is possible to detect problems through thermographies, but it is difficult to obtain an exact value of the losses.
Energy Efficiency in Boilers
01
3

## Slide 38
Condensate heat recovery:
For every kg of condensate that does not return to the inlet tank, it must be replaced with a new 1 kg of water at room temperature, which must be heated again with energy.
Energy Efficiency in Boilers
01
4

## Slide 39
Condensate heat recovery:
EXAMPLE-.
Calculation of savings by recovering 1000 kg/h of condensate from the purges at 4bar.
Information: | 
A- Condensate pressure | 4 bar
B- Enthalpy of the condensate | 605 kJ/kg
C- Energy losses in the return | 20%
D- Enthalpy of the contribution water to the boiler (20ºC) | 84 kJ/kg
E- Condensate flow | 1.000 kg/h
F- Fuel cost | 0,03 €/kWh
G- Water cost and treatment | 0,80 €/m3
H- Hours of operation | 4.000 h/year
I- Boiler performance | 90%
Calculations: | 
J- Recovered Energy: ((B x 0,80)-D) x E x H | 1.600.000.000 kJ/year
K- Energy saving: (J/I) / 3.600 kJ/kWh | 493.800 kWh/year
M- Energy and economic savings (K x F) | 14.800 €/year
N- Water cost savings and treatment (E/1.000) x G x H | 3.200 €/year
TOTAL SAVINGS: M + N | 18.000 €/year
4
Energy Efficiency in Boilers
01

## Slide 40
  Heat recovery from boiler purges:
BOILER
Energy Efficiency in Boilers
01
5

## Slide 41
  Heat recovery from boiler purges:
BOILER
15 bar
1,5 bar
EXAMPLE.
For a boiler that produces steam at 15 bar, it is proposed to take advantage of the purges (662 kg/h) in a flash tank at 1,5 bar. Calculate the kg/h that would be produced by flash steam.
Entalpía 15 b = 845 kJ/kg
Entalpía 1,5 b = 467 kJ/kg
Excess enthalpy (845 - 467) = 336 kJ/kg  partial vaporization
How much flash vapor? Excess enthalpy / Enthalpy vaporization water 1,5b · 100 = 336/2226,5 ·100 = 15% → 0,15 · 662kg/h = 100kg/h
How much energy does it contain? 100kg/h · 2693,6kJ/kg (steam enthalpy 1,5b) = 269.360 kJ/h
5
Eficiencia energética en calderas
01

## Slide 42
  Heat recovery from boiler purges:
BOILER
Energy Efficiency in Boilers
01
5

## Slide 43
Eficiencia energética en secadores
02

## Slide 44
Drying is defined as the removal of small amounts of water from a material through the application of heat.
This process can be carried out mainly by thermal methods.
The fluid used to dry normally is air. Water is usually removed by the circulation of air over the material.
There is a wide variety of dryers according to different parameters:
  Heat Transfer System
  Pressure
  Heat Transfer Mechanisms (convection, radiation, conduction)
Energy Efficiency in Dryers
02

## Slide 45
(1) salida de aire
(2) sensor
(3) cámara de secado
(4) base
(5) calentador
(6) inversor
(7) motor
(8) ventilador
(9) control
Q = air mass (kg)*(hi (kJ/kgºC) · Tinput(ºC) – ho (kJ/kgºC) · Toutput(ºC))
η = performance
Q= heat generated
b = inlet fuel flow (kg/h or Nm3/h)
PCI = lower heat value of fuel (kJ/Nm3)
Energy Efficiency in Dryers
02

## Slide 46
Inefficient solution
Energy Efficiency in Dryers
02
Discontinuous dryers (Dendy, 2001)
Air hot
Incoming air
Fan
Grain bed
Exhausted Air
Perforated Sheet

## Slide 47
Energy Efficiency in Dryers
02
Continuous dryers (Dendy, 2001)
Receiving deposit
Column Dryer without mixing
Column Dryer with mixing
Screw
Warm air
Air distribution chamber
Air distribution chamber
Discharge roll with adaptable Speed
Discharge roll with adaptable Speed
Screw conveyor
Screw conveyor

## Slide 48
GENERAL SAVING MEASURES
The efficiency will be better the higher the temperature at the entrance,
The waste heat produced by other equipment can be used for this purpose,
It is important to try to dry naturally before using the dryer,
It is important not to dry above the storage temperature,
The drying time will be shorter, the smaller the size of the product,
Regulation of combustion (explained in previous slides),
Recovery of heat from combustion fumes,
Isolation of dryers to minimize losses (drying chamber, external surface such as walls or ceiling).
Energy Efficiency in Dryers
02

## Slide 49
ENERGY SAVING MEASURES
Modification of operating conditions.
  Heat the drying gases as much as possible
  Increase the high moisture content in exhausted gasses.
  Use sensible and latent heat from the exhaust vapors to preheat the combustion air.
  Recover the sensible residual heat of the dry product.
  Pre-dry the product through natural or forced atmospheric flows.
  Recover another residual heat from the factory to warm the incoming air for better drying.
  Use the furnace or boiler gases.
Minimize drying
  Dry as little as possible. Do not reduce the humidity of product below what is necessary.
  Dry as little as possible. The product must be dried before putting it in the dryers.
Check the degree of drying
  It is necessary to study the drying curve of the product to ensure the balance between humidity and ambient temperature.
Energy Efficiency in Dryers
02

## Slide 50
MAXIMUM VALUES OF RELATIVE HUMIDITY TO STORE
These data depend on the weather conditions.
Energy Efficiency in Dryers
02
CEREAL | MAXIMUM RELATIVE HUMIDITY %
Wheat | 13,5%
Corn | 13,5%
Paddy Rice | 15%
Rice | 13%

## Slide 51
1
2
3
4
Energy Efficiency in Dryers
02
What parameters can be adjusted?
Air temperature
Air speed
Air humidity
Product size

## Slide 52
Towards a sustainable agro-food industry. Capacity building programmes in energy efficiency.